Sunsynk Inverter Class for pv_opt
using the solarsynk2 add-on for Home Assistant by martinville
Outstanding questions/issues or to be tested in red
Revision record (changes since last version in green):
Ver	Date	Details	By
1	17/2/2024	First version	MW
2	23/2/2024	Grid charge time x should be unticked for discharge according to Sunsynk. Inverter general description added, working modes clarified	MW
3	27/3/2024	MorneSaunders360 add-on. SellTime(x)Pac applies to discharge only. Charge current is limited by Grid Amps and Charge Amps. Work Mode must be changed in real time to enable battery export to grid	MW
4	29/3/2024	Grid charge on and Gen charge on must be specified as a pair. Hold_charge method added. Inverter attributes section rewritten	MW

# 1. General description of Sunsynk inverter
## 1.1 Input / output
Sunsynk inverters (e.g. ECCO 3.6kW hybrid inverter SYNK-3.6K-SG04LP1) have the following power inputs and outputs:
Direction	Name	Used for
Input	Solar PV	1 or 2 strings of Solar panels up to 350V DC
Output	Load	Uninterruptible Power Supply (UPS) / essential load i.e. power supply segregated from the grid which will continue to be supplied when the grid is down. Will normally be prioritised. Inverter has an optional ‘islanding mode signal’ which is on when the grid is down and an output which can be wired to a relay to disconnect inverter from grid and connect earth to neutral in the event of a grid outage (this reflects a strong history for the brand in southern Africa). When the grid becomes live again the inverter can detect it and automatically revert to grid mode after a delay. In simple domestic installations in the UK this output is not used because grid outages are uncommon and this requires segregated wiring in the house as well as some additional switches. This can cause confusion because ‘Load’ in Sunsynk terms refers to this UPS output only, not the normal house supply
Input/Output	Batteries	Numerous types and makes supported, including some types which are managed using voltage instead of State of Charge (SOC). In new UK domestic installations these would almost certainly be Lithium batteries with a battery management system and SOC support
Input/Output	Grid	Inverter is connected to the grid via a single circuit breaker on the consumer unit. Current can flow in either direction through this connection. Inverter distinguishes between Export and supply to non-essential loads in the house by using a CT clamp round the incoming live connection. Based on this it can supply just enough power to feed the domestic circuits if Export is disabled in the settings. To avoid transient currents flowing backwards through the meter (a problem in South Africa), it can maintain a configurable ‘Grid Trickle Feed’ flowing from the grid when it is also supplying the house from PV / battery. Export is also supported via the same connection
Input/Output	Auxiliary Load	This connection can be used either for input (Generator / Wind turbine) or output (a second segregated supply). If used for input, a box labelled ‘Gen’ can be ticked for each time slot in Timer mode to allow the batteries to be charged from this source. Peak shaving is supported (limit power take from Gen and supply the rest from the grid). If used for output, the software allows output to be turned on / off according to SOC settings

## 1.2 Inverter Parameters affecting import/export
Name	Options	What they do
Priority Load / {"energyMode": 0}	Priority Battery (1) / Priority Load (0)	Solar sent to batteries first / Solar sent to UPS Load first
Work Mode / {"sysWorkMode": 0}	Selling first (0) / Zero Export + Limit to Load only (1) / Limited to Home (2)	If timer is enabled and SOC > target SOC, battery will export until target SOC is reached / Battery used for UPS Load only (tbc) / Battery used for UPS and home but not export / [Solarsynk does not currently have a method of querying these settings so pv_opt can’t check them] / Work Mode cannot be set on a timer and must be changed to correct value in real time
Export Power Limiter / {"pvMaxLimit": 3600} (this appears to be correct but misleadingly named)	Normally set to the power of the inverter	If set lower, would reduce Export power from the figure against each Time slot / Solarsynk does not currently have a method of querying these settings so pv_opt can’t check it. pv_opt uses config.yaml parameters / "battery_current_limit_amps" / "inverter_power_watts" / to define limits
Use Timer / {"peakAndVallery": "1"}	Tickbox (1)	If ticked, enables 6 individual time slots which have: / Start time / Whether batteries should be charged or discharged from Grid (tickbox) / Whether batteries should be charged from Gen (Auxiliary) input (tickbox) / Target SOC / Power limit
Charge Amps (Battery settings) / {"batteryMaxCurrentCharge": 50}		Maximum charge current at battery voltage (presumably for all sources, not just Grid). Single setting for total of all batteries connected to inverter / Depends on rating of battery. Maximum determined by battery spec – normally set by installer and shouldn’t be changed / pv_opt has a config.yaml setting / "battery_current_limit_amps" / to avoid planning for more / Use Grid Amps to adjust actual charge rate
Grid Charge / {"sdChargeOn": 1} tbc	Tickbox (1)	Whether batteries can be charged from grid. Normally set to 1 by installer and not changed
Grid Amps(0-275A) / {"sdBatteryCurrent": 50}		Charge current at battery voltage for charging from Grid. Will be limited to a maximum of Charge Amps Grid Amps should be adjusted to fill timer slot – if not, charging will stop but battery cannot output to home so will import from Grid. Also, lower current will increase battery life
Discharge Amps (Battery settings) / {"batteryMaxCurrentDischarge": 50} tbc		Maximum discharge current at battery voltage. On 2 x 5.12kWh batteries this was set to 90A by installer (=4.5kW) so won’t limit forced discharge on a 3.6kW inverter. For a single battery the max figure from the data sheet is 100A but if set to 50A (e.g. to increase battery life) would limit discharge power to 2.5kW

### 1.3 Time of use mode
Sunsynk inverters have 6 timeslots to cover a single 24 hour period when Timer is enabled. Each one has a settable start time; the end time of the previous slot adjusts automatically to match. This means that adjacent slots are contiguous and later slots start after earlier ones. Slot 1 can be set to start before 00:00 but Sunsynk advise against this. I haven’t tested this and I don’t know whether the end of slot 6 would always be 00:00 or the start of slot 1. It may be possible to set the timeslots to cover more than 1 day (I haven’t tested this) but this should be avoided as the results would be unpredictable. I think it is possible for one or more slots to contain 00:00 – 00:00 but I haven’t tested this. There is a ‘Use Timer’ mode tickbox to enable the timers. It may be possible to force a charge or discharge by changing Work Mode without using the timers but I haven’t tested this as the inverter then has no way to set Target SOC except for 100% when charging and Shudown Capacity when discharging
### 1.4 Live Price options
The Sunsynk app has a ‘Live Price’ mode which supports Octopus Flux and Octopus Agile. These are managed in the cloud so presumably work by setting Timer and SOC values on the inverter. I haven’t tried these yet but I believe the Flux option would use the timers to charge to 100% in the cheap window, discharge to say 20% in the Peak, and maintain a minimum 20% the rest of the time (a total of at least 4 slots). The Agile option seems to be a work in progress, there have been some problems with it. User can set min price for exporting from battery and max price for charging. I’ve heard that this works by updating the first 2 slots every 30mins (and presumably leaving the other 4 set to 00:00 – 00:00 but I haven’t tested this). As far as I can see it doesn’t take forecast PV into account so is less efficient than pv_opt

# 2. Sunsynk Integrations / Add-ons for Home Assistant
I know of 3 Sunsynk integrations for Home Assistant:
## 2.2 Deye/Sunsynk Home Assistant add-on by kellerza in GitHub
This requires a direct connection to the inverter via RS485
I didn’t use this one because it requires direct wiring and in some more modern Sunsynk inverters needs to share a single port on the inverter with a cable to the battery
## 2.3 Solar-Sunsynk Home Assistant integration by MorneSaunders360 in GitHub
I haven’t tried this and don’t know much about it but it uses the Sunsynk.net cloud API and has a Home Assistant Service which can be called to adjust inverter settings

## 2.4 Solarsynk2 add-on by martinville in GitHub
### 2.4.1 Connection method
Connects to the inverter via the Sunsynk.net cloud API used by the Sunsynk app. (nb Sunsynk have recently completed a migration from a Solarman integration which used a Solarman WiFi dongle. They refer to this as ‘Region 1’. Solarsynk2 only works with the Sunsynk API, known as ‘Region 2’). Data in the cloud is updated every 5 mins by a Sunsynk branded WiFi datalogger directly connected to the inverter. Consequently, the add-on is also set by default to poll the cloud every 5 mins
### 2.4.2 Updates
Updates to inverter settings are sent to the cloud by the same 5 min batch process. The add-on checks to see if any settings have been populated in a Helper called input_text.solarsynk_{inverter_sn}_settings. {inverter_sn} is defined manually in the pv_opt config. Data is in json format e.g:

{"sellTime2": "02:30","sellTime2Pac": "3599"}

If so, it posts them to the cloud, outputs the response to the log, and empties the Helper. Output is like this (inverter serial number redacted):

Updating Helper: input_text.solarsynk_xxxxxxxxxx_inverter_settings with: {"sellTime2": "02:30","sellTime2Pac": "3599"} / { / "code": 0, / "msg": "Success", / "data": null, / "success": true / } / Clearing previously set temporary settings.

It is possible to update multiple settings at the same time but by default the Helper is limited to 100 text chars. When the batch process runs and posts the commands, response from Sunsynk cloud to Solarsynk log is immediate and normally the inverter is updated seconds later

I asked martinville if he would add a real time method of update. He says he is limited by the technology of the add-on (a Bash script) and doesn’t want to make major alterations to the project but will give it some thought
### 2.4.3 Required Class attributes
NB in the notes below the settings for each of the timed slots are denoted by setting(x) where (x) is 1-6. The brackets should be ignored e.g
sellTime(x) = sellTime1, sellTime2, sellTime3, sellTime4, sellTime5, sellTime6
time(x)on = time1on, time2on, time3on, time4on, time5on, time6on
and so on

pv_opt attribute	Solarsynk entity	Sunsynk json key	Comments
.config
maximum_dod_percent	There isn’t a sensor for this but battery_current_limit_amps can be hard coded in config.yaml / Don’t use / sensor.solarsynk_{inverter_sn}_battery_shutdown_cap because battery will shut down	Low Batt: {"batteryLowCap": 20} / Battery Shutdown cap:{"batteryShutdownCap": 15}	Low battery warning % (e.g. 20) / Shutdown % (e.g. 15) / Sunsynk L5.1 datasheet has Min DOD 10%
update_cycle_seconds	Refresh_rate: 300		In Solarsynk yaml
supports_hold_soc			There isn’t a ‘mode’ for this but can be achieved using timers
id_battery_soc	sensor.solarsynk_{inverter_sn}_battery_soc		Current SOC
id_consumption_today	sensor.solarsynk_{inverter_sn}_day_load_energy		kWh since midnight
id_grid_import_today	sensor.solarsynk_{inverter_sn}_day_grid_import		kWh imported from grid since midnight
id_grid_export_today	sensor.solarsynk_{inverter_sn}_day_grid_export		kWh exported to grid since midnight
.brand_config
battery_voltage	sensor.solarsynk_{inverter_sn}_battery_voltage		Current battery voltage
id_timed_charge_start_hours	sensor.solarsynk_{inverter_sn}_prog(x)_time	"sellTime(x)": "16:00"	6 slots, (x) = 1-6. Contains both hours and minutes in the form hh:mm
id_timed_charge_start_minutes			See above
id_timed_charge_end_hours		"sellTime(x+1)": "19:00"	No separate setting – it is defined by the start time of the next slot i.e. x+1
id_timed_charge_end_minutes			See above
id_timed_charge_current	Solarsynk does not have a sensor for this – use "battery_current_limit_amps" in pv_opt config.yaml	Grid Amps {"sdBatteryCurrent": 50}	Will be limited by Battery Charge Amps in battery management system
.status	sensor.solarsynk_2206179621_overall_state	Normal or Offline
charge	active	sensor.solarsynk_{inverter_sn}_progx_charge	x is 1-6 for timer x / true if Grid charge is ticked (i.e. timer is enabled for charge)
	start	sensor.solarsynk_{inverter_sn}_progx_time	x is 1-6 for timer x
	end	sensor.solarsynk_{inverter_sn}_prog(x+1)_time	x is 1-6 for timer x / Not set explicitly but defined by the start of the next timer or Timer1 if x = 6)
	power	sensor.solarsynk_{inverter_sn}_battery_power Positive (charge) or negative (discharge). This is the total of individual batteries sampled at 5min intervals	There is no Solarsynk sensor for the power setting of a timeslot although this is settable
	target soc	sensor.solarsynk_{inverter_sn}_progx_capacity	x is 1-6 for timer x
discharge	active	sensor.solarsynk_{inverter_sn}_progx_charge	x is 1-6 for timer x / false if Grid charge is unticked (i.e. timer is enabled for discharge)
	start	sensor.solarsynk_{inverter_sn}_progx_time	x is 1-6 for timer x
	end	sensor.solarsynk_{inverter_sn}_prog(x+1)_time	x is 1-6 for timer x / Not set explicitly but defined by the start of the next timer or Timer1 if x = 6)
	power	sensor.solarsynk_{inverter_sn}_battery_power Positive (charge) or negative (discharge). This is the total of individual batteries sampled at 5min intervals	There is no Solarsynk sensor for the power setting of a timeslot although this is settable
	target soc	sensor.solarsynk_{inverter_sn}_progx_capacity	x is 1-6 for timer x
hold_soc	active
	soc	sensor.solarsynk_{inverter_sn}_battery_soc gives current SOC (total all batteries)

### 2.4.4 Required Class methods
NB the usual manual way to set a timed charge for a Sunsynk inverter / battery system is to set Grid Charge Amps to an appropriate level for the timed slot and use a target SOC to turn off when the desired state is reached. For discharging the usual manual method is to set power to an appropriate level for the timed slot and use a low target SOC to turn off when complete (say 20% which is the default shutdown SOC for the battery).
Work Mode is normally set to Limited to Home =2 which prevents export from battery but still allows export of excess Solar. To deliberately discharge the battery to the Grid, Work Mode should be set to Selling First = 0 in real time at the start of the timed slot and back to Limited to Home = 2 at the end This can only be done in real time, there is no option for this in the timer
Which timeslots to use? The timeslots need to avoid overlap, be in the right order, and cover 24 hours so all 6 should be set at the same time. Not all slots have to be used – they can be set 00:00 – 00:00
For Octopus Flux we need 5:
- 1. 00:00 – start charge
- 2. start charge – end charge
- 3. end charge to start discharge
- 4. start discharge – end discharge
- 5. end discharge – 00:00
- 6. not required so should be 00:00
For Octopus Agile we could use:
- 1. 00:00 – this 30min
- 2. this 30min – next 30min
- 3. 30min slot 2
- 4. 30min slot 3
- 5. 30min slot 4
- 6. end 30min slot 4 – 00:00

Normally we want battery to be available to power the home if Solar is insufficient so unless deliberately charging from the Grid, timed slots should be set to discharge. To avoid exporting to the Grid, Work Mode must be set to Limited to Home = 2. To export from Battery to the Grid, Work Mode must be changed to Selling First = 0 at the start of the timed slot and back to Limited to Home = 2 at the end

pv_opt method	Parameter / relevant Solarsynk entities	Sunsynk fields to update	Steps
.enable_timed_mode()	sensor.solarsynk_{inverter_sn}_use_timer / sensor.solarsynk_{inverter_sn}_battery_type / sensor.solarsynk_{inverter_sn}_overall_state / sensor.solarsynk_{inverter_sn}_grid_connected_status / Solarsynk doesn’t currently have a sensor for this	{"peakAndVallery": "1"} / nb spelling as above – it’s spelled wrong in the Sunsynk API / {"battMode": "-1"} tbc	Tick ‘Use Timer’ if not already ticked / In addition, check that: / 1. Battery type is Lithium. This ensures battery supports SOC sensor.solarsynk_{inverter_sn}_battery_type = 1. / 2. Inverter state is Normal / 3. Grid connection status = 1 / 4. Ideally we would check that the Auxiliary input/output is not connected but Solarsynk doesn’t currently have a method for this so the best we can do is disable charge from Gen in the timers
.control_charge() / The instructions given here will charge from Grid. Charging from PV happens automatically	Set / Start time for relevant slot (x) sensor.solarsynk_{inverter_sn}_prog(x)_time / Start time for next slot / sensor.solarsynk_{inverter_sn}_prog(x+1)_time / Tick Grid charge time (x) / sensor.solarsynk_{inverter_sn}_prog(x)_charge / Confirm untick Gen charge time (x) (works as a pair with Grid time x on – they must be sent together) / Set target SOC for this slot sensor.solarsynk_{inverter_sn}_prog(x)_capacity / Set Max Grid Amps for charging	"sellTime(x)": "02:00" / "sellTime(x+1)": "05:00" / "time(x)on": true / "genTime(x)on": false / "cap(x)": "80" / {"sdBatteryCurrent": 50}	Battery will charge from Grid during this time slot if current SOC is lower than target SOC(x) e.g. "cap(x)": "100" / Setting a time automatically sets end time for previous slot / Labelled ‘Grid’ with a tickbox next to each timer on inverter and ‘Grid Charge Time(x)’ in app / Labelled ‘Gen’ with a tickbox next to each timer on inverter and ‘Gen Charge Time(x)’ in app / Target State of Charge / In this mode, battery will not supply home so inverter will import from Grid to feed home / NB sellTime(x)Pac applies to discharge only, not charge
.control_discharge() / If timers are in use (they normally are), the instructions give here will discharge the batter to home until the end of the timeslot or the target SOC is reached / If target SOC is reached before the end of the slot, battery output will stop and inverter will start to import from the Grid to feed home. To avoid this, power should be adjusted to fill the slot / Work Mode is normally set to 2 = Limited to Home. If batteries are to be discharged for Export, setting Work Mode to ‘Selling First’ will additionally export to Grid	Set :- / Start time for relevant slot (x) sensor.solarsynk_{inverter_sn}_prog(x)_time / Start time for next slot (automatically sets end time for this slot) / sensor.solarsynk_{inverter_sn}_prog(x+1)_time / Untick Grid for relevant slot (x) / sensor.solarsynk_{inverter_sn}_prog(x)_charge / Confirm untick Gen charge time (x) (works as a pair with Grid time x on – they must be sent together) / Target SOC for this slot sensor.solarsynk_{inverter_sn}_prog(x)_capacity / Set Power for this slot / At the start of the slot, set Work Mode to 0 = Selling First / At the end of the slot, set Work Mode back to 2 = Limited to Home at the end in real time / There is no Solarsynk sensor for this. Don’t use Battery shutdown limit as we don’t want the battery to actually shut down	"sellTime(x)": "16:00" / "sellTime(x+1)": "19:00" / "time(x)on": false Labelled ‘Grid’ with a tickbox next to each timer on inverter and ‘Grid Charge Time(x)’ in app / "genTime(x)on": false / "cap(x)": "20" / "sellTime(x)Pac": "3600" / "sysWorkMode": 0 / "sysWorkMode": 2 / maximum_dod_percent	Same timeslots as above but Grid is unticked and Target SOC is lower. Battery will discharge to grid during this time slot if current SOC is higher than target SOC(x) e.g "cap(x)": "20" / Labelled ‘Gen’ with a tickbox next to each timer on inverter and ‘Gen Charge Time(x)’ in app / Should be no higher than Export Power Limiter but there is currently no method in Solarsynk to query this. Limited by hard coded settings in pv_opt config.yaml / Also should check that target SOC is not lower than Low Battery warning level / Limited by hard-coded setting in pv_opt config.yaml maximum_dod_percent
.hold_soc() / (no discharge) / The instructions given here will retain the current charge in the battery – no export, no import and no output to home. PV will continue to supply home, then battery then export to grid when battery is full	Start time for relevant slot (x) sensor.solarsynk_{inverter_sn}_prog(x)_time / Start time for next slot (automatically sets end time for this slot) / Untick Grid for relevant slot (x) / Confirm untick Gen charge time (x) (works as a pair with Grid time on – they must be sent together) / Set target SOC for this slot to 100% (or = current value in sensor.solarsynk_{inverter_sn}_progx_capacity)	"sellTime(x)": "16:00" / "sellTime(x+1)": "19:00" / "time(x)on": false Labelled ‘Grid’ with a tickbox next to each timer on inverter and ‘Grid Charge Time(x)’ in app / "genTime(x)on": false / "cap(x)": "100"	Same timeslots as above. Grid and Gen are unticked. Battery will stop all output if SOC is less than or equal to the target
.hold_soc() / (discharge to home only) / The instructions given here will stop the battery exporting or importing to/from the Grid but will allow the battery to feed home until the end of the timed slot or until target SOC is reached. Battery will also continue to charge from PV and export when battery is full	Set :- / Start time for relevant slot (x) sensor.solarsynk_{inverter_sn}_prog(x)_time / Start time for next slot (automatically sets end time for this slot) / sensor.solarsynk_{inverter_sn}_prog(x+1)_time / Untick Grid for relevant slot (x) / sensor.solarsynk_{inverter_sn}_prog(x)_charge / Confirm untick Gen charge time (x) (works as a pair with Grid time on – they must be sent together) / Target SOC for this slot to minimum -dod_percent / Power for this slot is not relevant and does not need to be set / At the start of the slot, check that Work Mode is set to 2 = Limited to home (should be set already since this is likely the setting unless exporting from battery)	"sellTime(x)": "16:00" / "sellTime(x+1)": "19:00" / "time(x)on": false Labelled ‘Grid’ with a tickbox next to each timer on inverter and ‘Grid Charge Time(x)’ in app / "genTime(x)on": false / "cap(x)": "20" / "sellTime(x)Pac": "3600" / "sysWorkMode": 2	Same timeslots as above. Grid and Gen are unticked and SOC is lower than the target / Labelled ‘Gen’ with a tickbox next to each timer on inverter and ‘Gen Charge Time(x)’ in app